State of Delaware

Department of Natural Resources & Environmental Control

Division of Water Resources

Ground Water Discharges Section

Innovative and Alternative System Approval

ISSUED TO:	Bio-Microbics Incorporated

8450 Cole Parkway

Shawnee, KS 66227

Phone (913) 422-0707

Fax (913) 422-0808

FROM:	Jason Baumgartner – Environmental Scientist

Ground Water Discharges Section

FOR:		BioBarrier Membrane Bioreactor System 0.5, 1.0, and 1.5

## APPROVAL DATE:	  7/29/11

In accordance with the Regulations Governing the Design, Installation, and Operation of On-Site Wastewater Treatment and Disposal Systems (Regulations), an application dated December 21, 2010, has been submitted by Bio-Microbics, for approval of the BioBarrier advanced treatment units as an Innovative & Alternative On-Site Wastewater Treatment Units.

Based on the review of the application, the Department hereby grants approval of the use of the BioBarrier advanced treatment unit as an Innovative & Alternative On-Site Wastewater Treatment Unit subject to the conditions, limitations, and requirements set forth herein:

- Product Description

The BioBarrier unit is a membrane bioreactor that combines an activated sludge treatment process with solids separation properties of membrane filtration.  The membrane is submerged in the mixed liquor and provides a barrier that retains microorganisms, allowing them to remain in the treatment process for long periods of time.  The large inventory of biological solids in the process provides a buffer for shock loading of organic matter.  The long residence time in the treatment system allows for the organisms to consume themselves, reducing the total amount of solids produced by the treatment process.  The aeration portion of the system provides for the mixing of the wastewater and organisms.  This mixing facilitates the contact between the organic contaminants in the wastewater and the organisms that provide for removal of the contaminants.

The various models have the treatment capacities shown in the following table:

| Model | Capacity (gallons per day - gpd) |
| --- | --- |
| BioBarrier MBR 0.5 | 500 |
| BioBarrier MBR 1.0 | 1000 |
| BioBarrier MBR 1.5 | 1500 |

2.	Claim

Approval is based on information submitted by the Manufacturer indicating the specified models will routinely provide effluent quality not exceeding 30 mg/l of BOD5, 30 mg/l of TSS, 20 mg/l of Total Nitrogen (TN), and fecal coliform levels less than 200 cfu/ml assuming influent loading does not exceed the treatment capabilities of the units.

This unit has been NSF 40 and 245 certified.

- Use and Design Criteria

    - The Bio-Microbics BioBarrier unit may be installed for new and replacement systems with conventional and innovative and/or alternative disposal systems.

    - An on-site wastewater treatment and disposal system permit application incorporating a Bio-Microbics BioBarrier unit shall be designed in accordance with the Regulations, and manufacturer’s specifications.  The design shall be completed by a DNREC Class C Design Engineer unless otherwise approved by the Department.  The permit application shall include proper unit specifications.

    - The designer must assure that the settling zone and treatment zone must have above grade access.  The BioBarrier module shall also have above grade access.  The design also must ensure that the control panel and blower are accessible.

    - The Bio-Microbics BioBarrier unit shall not be installed within areas subject to traffic loads unless specially designed on a case by case basis in accordance with the Regulations.

    - The manufacturer is responsible for providing the Department a list of all local distributors and their associated contact information.  This list must be kept current and shall be submitted to the Department on a yearly basis.

- Installation Procedures

- The Bio-Microbics BioBarrier unit shall be installed by a DNREC Class E System Contractor under the supervision of a manufacturer’s representative, or by a DNREC Class E System Contractor who has been certified for unit installation.  Proof of certification shall be provided in writing to the Department.

- The blower must be installed on a concrete base and located no more than 40 feet from the tank.

- Start up of the system and initial operational checks shall be conducted by the Class E System Contractor (trained by the manufacturer), Design Engineer, and a Ground Water Discharges Section (Large System Branch) representative.  If the Class E System Contractor is not certified, a manufacturer’s representative shall perform the operational checks of the system at start up.  If the manufacturer’s representative can not be on site at the time of start up, they must provide final start up approval to the Department in writing.

  - Operation and Maintenance

    - The Bio-Microbics BioBarrier unit shall be operated and maintained in accordance with the manufacturer’s specifications.  In accordance with the NSF approval, the manufacturer is responsible for maintaining this certification.

    - The manufacturer or manufacturer’s representative shall comply with all Department mandated requirements as specified in permit conditions.  This shall include operation and maintenance requirements.

  - Sampling and Approval

The Department reserves the right to sample any unit at any time.

  - General Conditions

    - Use of the system for wastes other than residential shall be on a case by case basis.

    - In the event that the product fails to perform as claimed by the applicant, and it is found that the system is installed and working as designed, and there is no toxicity in the waste; the use of the units for new installations shall cease.  Use of the units shall not resume until such time the applicant and the Department have reached an acceptable agreement for resolving the situations.

    - Any changes that deviate from the specifications as submitted with this approval shall be approved by the Department prior to use.